{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["技术要求","碎石机房隔断钢架防护工程量清单"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"技术要求","index":0,"n_rows":7,"n_cols":6,"rows_kept":7,"merged":[[0,0,0,5],[5,0,5,1],[5,2,5,5],[6,0,6,5]],"flags":["formulas_cached_only"]}
["采购项目清单：口腔CT机房和碎石机房放射防护改造工程"]
["序号","项目名称","数量或规模","资金预算（万元）","资金来源","备注（规格）"]
[1,"口腔CT机房和碎石机房放射防护改造工程","见清单",8.3,"自筹"]
[]
["合计"]
["备注"]
["技术要求及配置确认书\n一、项目名称、数量： 口腔CT机房和碎石机房放射防护改造工程 \n二、项目用途说明：               \n三、配置规格、附件及零配件（包括专用工具）： \n1、详情见后附工程量清单。2、工期为7天。              \n                                                       \n四、详细技术要求、参数及产品资料等：\n①、税务登记证、营业执照、组织机构代码或三证合一的营业执照。②、法人签字并加盖公章的委托书。③、被委托人的身份证。④、失信被执行人、重大税收违法案件当事人名单、政府采购严重违法失信行为记录名单查询记录（“信用中国”及“中国政府采购网”查询记录）。⑤、“近三年内参加招投标活动在经营活动中没有重大违法违纪记录”的书面声明。⑥、投标人必须具有射线防护工程施工能力，营业范围内包含射线防护工程施工。⑦、使用的产品须具备卫生主管部门出具的放射防护器材检测报告单。开标时，投标企业需提供上述证件的原件或复印件加公章由评委审验。            \n五、售后服务条件及交货日期（或工期）：\n①、质量承诺；②、响应院方工期要求，若承诺的工期不能按时完成，按合同约定进行处罚；③、安全承诺：施工中做好施工组织，保证安全生产，防止人为的对场区管网的损坏。如有安全事故或对场区管网损坏，其造成的伤害事故及一切经济损失，由施工企业承担全责；④、合同外增项按原招标优惠比率结算。                       \n\n五、推荐供应商清单\n一、除公开招标、单一来源外的其他院内采购方式，可推荐三家以上供应商，并且要具有可比性。\n二、填写内容包括供应商名称、联系人、联系方式，产地、品牌或资质。\n推荐供应商1                                              "]

{"sheet":"碎石机房隔断钢架防护工程量清单","index":1,"n_rows":19,"n_cols":4,"rows_kept":19,"merged":[[0,0,0,3],[3,0,5,0],[3,1,5,1],[3,3,5,3],[6,0,8,0],[6,1,8,1],[6,3,8,3],[9,0,12,0],[9,1,12,1],[9,3,12,3],[13,0,16,0],[13,1,16,1],[13,3,16,3],[17,0,18,0],[17,1,18,1],[17,3,18,3]],"flags":["formulas_cached_only"]}
["碎石机房隔断钢架墙防护工程量清单"]
["序号","项目名称","规格","工程量"]
[1,"拆除现有隔断层","4500*4350（高）","19.5㎡"]
[2,"新建方管钢架墙","1、尺寸：4500*4350（高）","19.5㎡"]
[null,null,"2、规格：40*60*2.5mm方钢"]
[null,null,"3、标准：立柱间距600mm"]
[3,"铅板防护施工","1、尺寸：4500×3450mm","19.5㎡"]
[null,null,"2、铅当量：2mmpb"]
[null,null,"3、铅板粘贴面拉毛→20mm细木工板发泡胶粘贴→自攻丝固定钢架→铅板盖覆盖钉孔"]
[4,"墙面装饰","1、部位：钢架隔断墙","39㎡"]
[null,null,"2、尺寸：4500×4350mm（高）"]
[null,null,"3、材质：面层防刮、抗菌、防潮、"]
[null,null,"4、施工工艺：20mm细木工板打底找平层→结构胶打点→双面胶辅助固定→结构胶美缝"]
[5,"不锈钢铅防护平开门","1、尺寸：800×2100mm   3mmpb","1樘"]
[null,null,"2、配套优质品牌不锈钢执手锁"]
[null,null,"3、其他小五金配件"]
[null,null,"4、整体不锈钢材质"]
[6,"原有装饰吊顶局部拆除及恢复","规格：600*600mm","1项"]
[null,null,"材质：铝扣板"]